## Fire ventilation
Mosen Ltd
Preliminary tunnel fire ventilation calculations
Version 1, 25-10-2017
For illustration purposes only - not for design. No responsibility for the use of this spreadsheet will be accepted by Mosen Ltd, to the maximum extent permissible by law.
Please contact us for your project design requirements: |  | www.mosen.global |  | info@mosen.global
Project: | XXX Tunnel
Subject:
Date:
Data:
Fire Size | = |  | 10 |  | MW
Design airflow velocity upstream of fire | = |  | 3 |  | m/s
Adverse wind speed against exit portal | = |  | 5 |  | m/s
Density of Air | = |  | 1.2 |  | kg/m^3
Tunnel Air Dynamic Pressure | = |  | 5.4 |  | Pa
Length of Tunnel | = |  | 2000 |  | m
Fire location (before exit portal) | = |  | 300 |  | m
Width of Tunnel | = |  | 14.95 |  | m
Drag factor Cd | = |  | 0.4
Tunnel Height | = |  | 5.5 |  | m
Tunnel Area A | = |  | 80 |  | m^2
Tunnel Hydraulic Diameter | = |  | 8.0416 |  | m
Tunnel friction factor 'f' | = |  | 0.025 |  | -
Car Area Ac | = |  | 2 |  | m^2
Truck Area At | = |  | 6 |  | m^2
Quantity cars Nc | = |  | 100 |  | /km/lane
Quantity trucks Nt | = |  | 7 |  | /km/lane
Area Vehicular Av | = |  | 2.2 |  | m^2
No. of Lanes N | = |  | 3
Gradient % | = |  | 2
Aerodynamic Calculations
Avg temperature downstream of fire | = |  | 673 |  | K
Tunnel Temperature | = |  | 293 |  | K
Density of Air | = |  | 0.52244 |  | kg/m^3
Velocity m/s | = |  | 6.8908 |  | m/s
Inlet velocity head | = |  | 5.4 |  | Pa
Exit velocity head | = |  | 12.4034 |  | Pa
Outlet Loss | = |  | 12.4034 |  | Pa
Losses With Fire
Inlet Losses | = |  | 2.7 |  | Pa
Frictional loss, section without fire | = |  | 28.5392 |  | Pa
Frictional loss, section with fire | = |  | 11.5681 |  | Pa
Vehicular Losses | = |  | 32.4146 |  | Pa
Wind Allowance | = |  | 15 |  | Pa
Loss at Tunnel Outlet | = |  | 12.4034 |  | Pa
Fire buoyancy pressure | = |  | 39.8814 |  | Pa
Blockage due to fire | = |  | 1.65 |  | Pa
Overall Losses | = |  | 144.1567 |  | Pa
Total Thrust | = |  | 11532.5342 |  | N
Conventional Jetfan Selection | [5 empty] | MoJet Selection
Conventional jetfan bench thrust | = |  | 1650 |  | N | MoJet bench thrust | = | 1650 | N
Jetfan diameter | = |  | 1.25 |  | mm | MoJet Diameter | = | 1.25 | m
Distance to tunnel soffit | = |  | 0.1 |  | m | Distance to tunnel soffit | = | 0.1 | m
Fan velocity | = |  | 34.2 |  | m/s | Fan velocity | = | 34.2 | m/s
Velocity factor | = |  | 0.91228 |  |  | Velocity factor | = | 0.91228
Installation factor | = |  | 0.67 |  |  | Installation factor | = | 0.95
Total bench thrust | = |  | 18867.8086 |  | N | Total bench thrust | = | 13306.7703 | N
Number of conventional jetfans required | = |  | 11.435 |  | nos | Number of MoJets required | = | 8.0647 | nos
Nearest whole number | = |  | 12 |  | nos | Nearest whole number | = | 9 | nos
Extra Row(Part 9 BD 78/99 pg 5/17) | = |  | 2 |  | nos | Extra Row (Part 9 BD 78/99 pg 5/17) | = | 2 | nos
Total number of conventional jetfans required | = |  | 14 |  | nos | Total number of MoJets required | = | 11 | nos
Conventional jetfan spacing (minimum) | = |  | 80.4156 |  | m | MoJet spacing (minimum) | = | 40.2078 | m
cased on 10 tun. dia BD 78/79 pg 5/11 | [5 empty] | based on 5 tunnel hydraulic diameters